## MethodDirect
Diagram | Inputs |  |  |  | Outputs |  |  |  | Check |  |  | w/ Dedicated Exhaust
| SWs | SWret | fo | Wo_min | W'o | Wo | Wrec | Wexh | %OA | Imbalance |  | Wdx | Imbalance
| 100 | 60 | 0.2 | 50 | 50 | 50 | 50 | 10 | 0.5 | 40 | Pressurized | 0 | 40 | Pressurized -->
INSTRUCTIONS:
Edit values in Input boxes to observe changes | [5 empty] | Wrec = 50
on the diagram.
Input boxes are formatted as shown below:
|  |  |  | Wo = 50 |  |  |  | Wexh = 10
[5 empty] | Ws = 100 |  | Wret = 60
Wdx = 0
Pressurized -->
Wbal = 40
BUILDING
EXAMPLES:
To create new examples, you can copy a row, insert it into the table, and modify copied values.
Example Cases | Inputs |  |  |  | Outputs |  |  |  | Check |  |  | w/ Dedicated Exhaust
| SWs | SWret | fo | Wo_min | W'o | Wo | Wrec | Wexh | %OA | Imbalance |  | Wdx | Imbalance
10% OA with fo = 0 | 100 | 90 | 0 | 0 | 0 | 10 | 90 | 0 | 0.1 | 10 | Pressurized | 0 | 10 | Pressurized
Min OA requirement | 100 | 90 | 0 | 20 | 20 | 20 | 80 | 10 | 0.2 | 10 | Pressurized | 5 | 5 | Pressurized
100% OA | 100 | 90 | 1 | 0 | 100 | 100 | 0 | 90 | 1 | 10 | Pressurized | 10 | 0 | Balanced
50% OA | 100 | 90 | 0.5 | 0 | 50 | 50 | 50 | 40 | 0.5 | 10 | Pressurized | 20 | -10 | Depressurized
0% OA | 100 | 100 | 0 | 10 | 10 | 10 | 90 | 10 | 0.1 | 0 | Balanced | 20 | -20 | Depressurized
Note on C3: Total supply airflow rate to building zones
Note on D3: Total return airflow rate from building zones
Note on E3: Outdoor Air Schedule value Between 0.0 and 1.0
Note on F3: Minimum OA Flow
Note on N3: Dedicated exhaust flow, e.g., via restroom exhaust
Note on C30: Total supply airflow rate to building zones
Note on D30: Total return airflow rate from building zones
Note on E30: Outdoor Air Schedule value Between 0.0 and 1.0
Note on F30: Minimum OA Flow
Note on N30: Dedicated exhaust flow, e.g., via restroom exhaust